## Summary Sheet
Summary Sheet - SEER and SCOP Data for FUJITSU J-IIS Heat Pump Systems
Model | Description | EER | *SEER | COP | SCOP
AJY040LCLAH | 4HP / 12.1kW Heat Pump | 3.52 | 6.1535 | 4.4 | 5.6534
AJY045LCLAH | 5HP / 14.0kW Heat Pump | 3.16 | 5.8095 | 4.07 | 5.1795
AJYA54LCLAH | 6HP / 15.1kW Heat Pump | 2.84 | 5.5356 | 3.87 | 4.8321
* SEER values based on a General Office Type Accommodation load profile as detailed in section 9 of the Non-Domestic Heating, Cooling and Ventilation Compliance Guide
Note that the J-IIS outdoor units have been optimised for improved performance at part
load conditions (not full load) which is why SEER & SCOP numbers are considerably better
than the EER & COP. Also note that J-IIS SEER & SCOP numbers are better than the equivalent
capacity J-II models for the same reasons.

## J-IIS SEER
FUJITSU J-IIS VRF SYSTEM
SEER DATA
Enter required quantity to reveal individual or cumulative results. | [11 empty] | Factory Data Input
[5 empty] | Cooling | [5 empty] | Cooling
| Model | Description | QTY | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ |  | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ | SEER
|  |  |  | Nom PI | [5 empty] | Nom PI
[5 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe J-IIs Heat Pump | AJY040LCLAH | 4HP Heat Pump | [7 empty] | 12.1 | 3.025 | 6.05 | 9.075 | 12.1 | 6.1535
[10 empty] | 3.44 | 0.42 | 0.85 | 1.68 | 3.44
| AJY045LCLAH | 5HP Heat Pump | [7 empty] | 14 | 3.5 | 7 | 10.5 | 14 | 5.8095
[10 empty] | 4.43 | 0.45 | 1.09 | 2.15 | 4.43
| AJY054LCLAH | 6HP Heat Pump | [7 empty] | 15.1 | 3.775 | 7.55 | 11.325 | 15.1 | 5.5356
[10 empty] | 5.32 | 0.51 | 1.23 | 2.44 | 5.03
| Total Project (VRF) Cooling Output |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  | 0 | 0 | 0 | 0 | 0
| Overall Energy Efficiency Ratio |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SEER
| Load Profile - Unknown |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  | 0% | 0% |  |  | 0

## J-IIS SCOP
FUJITSU J-IIS VRF SYSTEMS
SCOP DATA
Enter required quantity to reveal individual or cumulative results. | [10 empty] | Factory Data
[5 empty] | Heating | [5 empty] | Heating
| Model | Description | QTY | Nom Htg kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ |  | Nom HTG kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ | SCOP
|  |  |  | Nom PI | [5 empty] | Nom PI
[5 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe J-IIs Mini VRF Heat Pump | AJY040LCLAH | 4HP Heat Pump | [7 empty] | 13.6 | 3.4 | 6.8 | 10.2 | 12.3 | 5.6534
[10 empty] | 3.09 | 0.5 | 1.04 | 2.17 | 3.39
| AJY045LCLAH | 5HP Heat Pump | [7 empty] | 16 | 4 | 8 | 12 | 14.6 | 5.1795
[10 empty] | 3.93 | 0.66 | 1.33 | 2.75 | 4.32
| AJY054LCLAH | 6HP Heat Pump | [7 empty] | 16.5 | 4.125 | 8.25 | 12.375 | 4.52 | 4.8321
[10 empty] | 4.26 | 0.69 | 1.39 | 2.87 | 4.52
| Total Project (VRF) Cooling Output |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  | 0 | 0 | 0 | 0 | 0
| Overall COP |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SCOP
| Load Profile - Unknown |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined | [7 empty] | #DIV/0!