## Summary Sheet
Summary Sheet - SEER and SCOP Data for FUJITSU V-III Heat Pump Systems July 2015
Model | O/D Model Combinations | Description (Space Saving Combinations) | Nom Cooling kW | EER | *SEER | COP | SCOP
AJY72LALBH 1 module |  | 8HP Heat Pump System | 22.4 | 4.31 | 6.3159 | 4.84 | 5.5638
AJY90LALBH 1 module |  | 10HP Heat Pump System | 28 | 3.85 | 6.1199 | 4.35 | 5.3158
AJY108LALBH 1 module |  | 12HP Heat Pump System | 33.5 | 3.74 | 6.5455 | 4.34 | 5.6006
AJY126LALBH 1 module |  | 14HP Heat Pump System | 40 | 3.65 | 6.3733 | 4.03 | 5.7354
AJY144LALBH 1 module |  | 16HP Heat Pump System | 45 | 3.46 | 6.3913 | 3.67 | 5.3916
AJY162LALBH 1 module |  | 18HP Heat Pump System | 50 | 3.02 | 6.304 | 3.67 | 5.1686
AJY180LALBH 2 module | 90 + 90 | 20HP Heat Pump System | 56 | 3.85 | 6.1199 | 4.34 | 5.3158
AJY198LALBH 2 module | 126 + 72 | 22HP Heat Pump System | 62.4 | 3.86 | 6.3146 | 4.28 | 5.6489
AJY216LALBH 2 module | 126 + 90 | 24HP Heat Pump System | 68 | 3.73 | 6.2507 | 4.15 | 5.552
AJY234LALBH 2 module | 144 + 90 | 26HP Heat Pump System | 73 | 3.6 | 6.261 | 3.9 | 5.3557
AJY252LALH 2 module | 162 + 90 | 28HP Heat Pump System | 78 | 3.27 | 6.1863 | 3.9 | 5.2008
AJY270LALBH 2 module | 144 + 126 | 30HP Heat Pump System | 85 | 3.55 | 6.3817 | 3.83 | 5.543
AJY288LALBH 2 module | 144 + 144 | 32HP Heat Pump System | 90 | 3.46 | 6.3913 | 3.67 | 5.3916
AJY306LALBH 2 module | 162 + 144 | 34HP Heat Pump System | 95 | 3.21 | 6.3387 | 3.67 | 5.2695
AJY324LALBH 2 module | 162 + 162 | 36HP Heat Pump System | 100 | 3.02 | 6.304 | 3.67 | 5.1686
AJY342LALBH 3 module | 162 + 90 + 90 | 38HP Heat Pump System | 106.5 | 3.41 | 6.1527 | 4.02 | 5.2242
AJY360LALBH 3 module | 144 + 126 + 90 | 40HP Heat Pump System | 113 | 3.62 | 6.299 | 3.95 | 5.4819
AJY378LALBH 3 module | 144 + 144 + 90 | 42HP Heat Pump System | 118 | 3.54 | 6.3062 | 3.81 | 5.3683
AJY396LALBH 3 module | 162 + 144 + 90 | 44HP Heat Pump System | 123 | 3.34 | 6.2591 | 3.81 | 5.27
AJY414LALBH 3 module | 162 + 162 + 90 | 46HP Heat Pump System | 130 | 3.17 | 6.2242 | 3.81 | 5.1854
AJY432LALBH 3 module | 144 + 144 + 144 | 48HP Heat Pump System | 135 | 3.46 | 6.3913 | 3.67 | 5.3916
AJY450LALBH 3 module | 162 + 144 + 144 | 50HP Heat Pump System | 140 | 3.29 | 6.3539 | 3.67 | 5.3076
AJY468LALBH 3 module | 162 + 162 + 144 | 52HP Heat Pump System | 145 | 3.14 | 6.3254 | 3.67 | 5.2338
AJY486LALBH 3 module | 162 + 162 + 162 | 54HP Heat Pump System | 150 | 3.02 | 6.304 | 3.67 | 5.1686
* SEER values based on a General Office Type Accomodation load profile as detailed in section 9 of the Non-Domestic Heating, Cooling and Ventilation Compliance Guide
Model | O/D Model Combinations | Description (Energy Efficiency Combinations) | Nom Cooling kW | EER | *SEER | COP | SCOP
AJY144LALBHH 2 module | 72 + 72 | 16HP Heat Pump System | 44.8 | 4.31 | 6.3159 | 4.84 | 5.5638
AJY162LALBHH 2 module | 90 + 72 | 18HP Heat Pump System | 50.4 | 4.04 | 6.1984 | 4.55 | 5.4186
AJY180LALBHH 2 module | 108 + 72 | 20HP Heat Pump System | 55.9 | 3.95 | 6.4362 | 4.52 | 5.5791
AJY216LALBHH 3 module | 72 + 72 + 72 | 24HP Heat Pump System | 67.2 | 4.31 | 6.3159 | 4.84 | 5.5638
AJY234LALBHH 3 module | 90 + 72 + 72 | 26HP Heat Pump System | 72.8 | 4.12 | 6.2321 | 4.63 | 5.4611
AJY252LALBHH 3 module | 108 + 72 + 72 | 28HP Heat Pump System | 78.3 | 4.04 | 6.3967 | 4.61 | 5.5728
AJY270LALBHH 3 module | 126 + 72 + 72 | 30HP Heat Pump System | 84.8 | 3.97 | 6.3022 | 4.42 | 5.633
AJY288LALBHH 3 module | 108 + 108 + 72 | 32HP Heat Pump System | 89.4 | 3.87 | 6.4743 | 4.45 | 5.5861
AJY306LALBHH 3 module | 126 + 108 + 72 | 34HP Heat Pump System | 95.9 | 3.82 | 6.3915 | 4.3 | 5.6392
AJY324LALBHH 3 module | 108 + 108 + 108 | 36HP Heat Pump System | 100.5 | 3.74 | 6.5455 | 4.34 | 5.6011
AJY342LALBHH 3 module | 126 + 108 + 108 | 38HP Heat Pump System | 107 | 3.7 | 6.4706 | 4.21 | 5.6479
AJY360LALBHH 3 module | 126 + 126 + 108 | 40HP Heat Pump System | 113.5 | 3.68 | 6.4148 | 4.11 | 5.6929
AJY378LALBHH 3 module | 126 + 126 + 126 | 42HP Heat Pump System | 120 | 3.65 | 6.3733 | 4.03 | 5.7353
AJY396LALBHH 3 module | 144 + 126 + 126 | 44HP Heat Pump System | 125 | 3.58 | 6.3787 | 3.89 | 5.6016
AJY414LALBHH 3 module | 144 + 144 + 126 | 46HP Heat Pump System | 130 | 3.52 | 6.3848 | 3.77 | 5.4887
* SEER values based on a General Office Type Accomodation load profile as detailed in section 9 of the Non-Domestic Heating, Cooling and Ventilation Compliance Guide

## SEER Space Saving Combos
FUJITSU V-III VRF SYSTEMS
SEER DATA
Enter required quantity to reveal individual or cumulative results.
| Space Saving Combinations | [11 empty] | Input Data
[6 empty] | Cooling | [5 empty] | Cooling
| Model | Multiple Module Combinations | Description | QTY | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ |  | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ | SEER
[5 empty] | Nom PI | [5 empty] | Nom PI
[6 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe V-III Heat Pump Space Saving Combinations | AJY72LALBH 1 module |  | 8HP Heat Pump System | [7 empty] | 22.4 | 5.6 | 11.2 | 16.8 | 22.4 | 6.3159
[11 empty] | 5.2 | 0.95 | 1.6 | 2.56 | 5.2
| AJY90LALBH 1 module |  | 10HP Heat Pump System | [7 empty] | 28 | 7 | 14 | 21 | 28 | 6.1199
[11 empty] | 7.28 | 1.14 | 1.97 | 3.59 | 7.28
| AJY108LALBH 1 module |  | 12HP Heat Pump System | [7 empty] | 33.5 | 8.375 | 16.75 | 25.125 | 33.5 | 6.5455
[11 empty] | 8.96 | 1.23 | 2.17 | 4.11 | 8.96
| AJY126LALBH 1 module |  | 14HP Heat Pump System | [7 empty] | 40 | 10 | 20 | 30 | 40 | 6.3733
[11 empty] | 10.96 | 1.31 | 2.73 | 5.42 | 10.96
| AJY144LALBH 1 module |  | 16HP Heat Pump System | [7 empty] | 45 | 11.25 | 22.5 | 33.75 | 45 | 6.3913
[11 empty] | 13.01 | 1.41 | 3.1 | 6.11 | 13.01
| AJY162LALBH 1 module |  | 18HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 50 | 6.304
[11 empty] | 16.56 | 1.46 | 3.46 | 7.37 | 16.56
| AJY180LALBH 2 module | 90 + 90 | 20HP Heat Pump System | [7 empty] | 56 | 14 | 28 | 42 | 56 | 6.1199
[11 empty] | 14.56 | 2.28 | 3.94 | 7.18 | 14.56
| AJY198LALBH 2 module | 126 + 72 | 22HP Heat Pump System | [7 empty] | 62.4 | 15.6 | 31.2 | 46.8 | 62.4 | 6.3146
[11 empty] | 16.16 | 2.26 | 4.33 | 7.98 | 16.16
| AJY216LALBH 2 module | 126 + 90 | 24HP Heat Pump System | [7 empty] | 68 | 17 | 34 | 51 | 68 | 6.2507
[11 empty] | 18.24 | 2.45 | 4.7 | 9.01 | 18.24
| AJY234LALBH 2 module | 144 + 90 | 26HP Heat Pump System | [7 empty] | 73 | 18.25 | 36.5 | 54.75 | 73 | 6.261
[11 empty] | 20.29 | 2.55 | 5.07 | 9.7 | 20.29
| AJY252LALH 2 module | 162 + 90 | 28HP Heat Pump System | [7 empty] | 78 | 19.5 | 39 | 58.5 | 78 | 6.1863
[11 empty] | 23.84 | 2.6 | 5.43 | 10.96 | 23.84
| AJY270LALBH 2 module | 144 + 126 | 30HP Heat Pump System | [7 empty] | 85 | 21.25 | 42.5 | 63.75 | 85 | 6.3817
[11 empty] | 23.97 | 2.72 | 5.83 | 11.53 | 23.97
| AJY288LALBH 2 module | 144 + 144 | 32HP Heat Pump System | [7 empty] | 90 | 22.5 | 45 | 67.5 | 90 | 6.3913
[11 empty] | 26.02 | 2.82 | 6.2 | 12.22 | 26.02
| AJY306LALBH 2 module | 162 + 144 | 34HP Heat Pump System | [7 empty] | 95 | 23.75 | 47.5 | 71.25 | 95 | 6.3387
[11 empty] | 29.57 | 2.87 | 6.56 | 13.48 | 29.57
| AJY324LALBH 2 module | 162 + 162 | 36HP Heat Pump System | [7 empty] | 100 | 25 | 50 | 75 | 100 | 6.304
[11 empty] | 33.12 | 2.92 | 6.92 | 14.74 | 33.12
| AJY342LALBH 3 module | 162 + 90 + 90 | 38HP Heat Pump System | [7 empty] | 106 | 26.5 | 53 | 79.5 | 106 | 6.1527
[11 empty] | 31.12 | 3.74 | 7.4 | 14.55 | 31.12
| AJY360LALBH 3 module | 144 + 126 + 90 | 40HP Heat Pump System | [7 empty] | 113 | 28.25 | 56.5 | 84.75 | 113 | 6.299
[11 empty] | 31.25 | 3.86 | 7.8 | 15.12 | 31.25
| AJY378LALBH 3 module | 144 + 144 + 90 | 42HP Heat Pump System | [7 empty] | 118 | 29.5 | 59 | 88.5 | 118 | 6.3062
[11 empty] | 33.3 | 3.96 | 8.17 | 15.81 | 33.3
| AJY396LALBH 3 module | 162 + 144 + 90 | 44HP Heat Pump System | [7 empty] | 123 | 30.75 | 61.5 | 92.25 | 123 | 6.2591
[11 empty] | 36.85 | 4.01 | 8.53 | 17.07 | 36.85
| AJY414LALBH 3 module | 162 + 162 + 90 | 46HP Heat Pump System | [7 empty] | 128 | 32 | 64 | 96 | 128 | 6.2242
[11 empty] | 40.4 | 4.06 | 8.89 | 18.33 | 40.4
| AJY432LALBH 3 module | 144 + 144 + 144 | 48HP Heat Pump System | [7 empty] | 135 | 33.75 | 67.5 | 101.25 | 135 | 6.3913
[11 empty] | 39.03 | 4.23 | 9.3 | 18.33 | 39.03
| AJY450LALBH 3 module | 162 + 144 + 144 | 50HP Heat Pump System | [7 empty] | 140 | 35 | 70 | 105 | 140 | 6.3539
[11 empty] | 42.58 | 4.28 | 9.66 | 19.59 | 42.58
| AJY468LALBH 3 module | 162 + 162 + 144 | 52HP Heat Pump System | [7 empty] | 145 | 36.25 | 72.5 | 108.75 | 145 | 6.3254
[11 empty] | 46.13 | 4.33 | 10.02 | 20.85 | 46.13
| AJY486LALBH 3 module | 162 + 162 + 162 | 54HP Heat Pump System | [7 empty] | 150 | 37.5 | 75 | 112.5 | 150 | 6.304
[11 empty] | 49.68 | 4.38 | 10.38 | 22.11 | 49.68
| Total Project (VRF) Cooling Output |  |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  |  | 0 | 0 | 0 | 0 | 0
| Overall Energy Efficiency Ratio |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SEER
| Load Profile - Unknown |  |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!

## SEER Energy Efficient Combos
FUJITSU V-III VRF SYSTEM
SEER DATA
Enter required quantity to reveal individual or cumulative results.
| Energy Efficiency Combinations | [11 empty] | Input Data
[6 empty] | Cooling | [5 empty] | Cooling
| Model | Multiple Module Combinations | Description | QTY | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ |  | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ | SEER
[5 empty] | Nom PI | [5 empty] | Nom PI
[6 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
| AJY72LALBH |  | 8HP Heat Pump System | [7 empty] | 22.4 | 5.6 | 11.2 | 16.8 | 22.4 | 6.3159
[11 empty] | 5.2 | 0.95 | 1.6 | 2.56 | 5.2
| AJY90LALBH |  | 10HP Heat Pump System | [7 empty] | 28 | 7 | 14 | 21 | 28 | 6.1199
[11 empty] | 7.11 | 1.14 | 1.97 | 3.59 | 7.28
| AJY108LALBH |  | 12HP Heat Pump System | [7 empty] | 33.5 | 8.375 | 16.75 | 25.125 | 33.5 | 6.5455
[11 empty] | 9.75 | 1.23 | 2.17 | 4.11 | 8.96
| AJY126LALBH |  | 14HP Heat Pump System | [7 empty] | 40 | 10 | 20 | 30 | 40 | 6.3733
[11 empty] | 11.34 | 1.31 | 2.73 | 5.42 | 10.96
| AJY144LALBH |  | 16HP Heat Pump System | [7 empty] | 45 | 11.25 | 22.5 | 33.75 | 45 | 6.3913
[11 empty] | 13.61 | 1.41 | 3.1 | 6.11 | 13.01
| AJY162LALBH |  | 18HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 50 | 6.304
[11 empty] | 16.56 | 1.46 | 3.46 | 7.37 | 16.56
2-pipe V-III H. Pump Energy Efficiency Combos | AJY144LALBHH 2 module | 72 + 72 | 16HP Heat Pump System | [7 empty] | 44.8 | 11.2 | 22.4 | 33.6 | 44.8 | 6.3159
[11 empty] | 10.4 | 1.9 | 3.2 | 5.12 | 10.4
| AJY162LALBHH 2 module | 90 + 72 | 18HP Heat Pump System | [7 empty] | 50.4 | 12.6 | 25.2 | 37.8 | 50.4 | 6.1984
[11 empty] | 12.48 | 2.09 | 3.57 | 6.15 | 12.48
| AJY180LALBHH 2 module | 108 + 72 | 20HP Heat Pump System | [7 empty] | 55.9 | 13.975 | 27.95 | 41.925 | 55.9 | 6.4362
[11 empty] | 14.16 | 2.18 | 3.77 | 6.67 | 14.16
| AJY216LALBHH 3 module | 72 + 72 + 72 | 24HP Heat Pump System | [7 empty] | 67.2 | 16.8 | 33.6 | 50.4 | 67.2 | 6.3159
[11 empty] | 15.6 | 2.85 | 4.8 | 7.68 | 15.6
| AJY234LALBHH 3 module | 90 + 72 + 72 | 26HP Heat Pump System | [7 empty] | 72.8 | 18.2 | 36.4 | 54.6 | 72.8 | 6.2321
[11 empty] | 17.68 | 3.04 | 5.17 | 8.71 | 17.68
| AJY252LALBHH 3 module | 108 + 72 + 72 | 28HP Heat Pump System | [7 empty] | 78.3 | 19.575 | 39.15 | 58.725 | 78.3 | 6.3967
[11 empty] | 19.36 | 3.13 | 5.37 | 9.23 | 19.36
| AJY270LALBHH 3 module | 126 + 72 + 72 | 30HP Heat Pump System | [7 empty] | 84.8 | 21.2 | 42.4 | 63.6 | 84.8 | 6.3022
[11 empty] | 21.36 | 3.21 | 5.93 | 10.54 | 21.36
| AJY288LALBHH 3 module | 108 + 108 + 72 | 32HP Heat Pump System | [7 empty] | 89.4 | 22.35 | 44.7 | 67.05 | 89.4 | 6.4743
[11 empty] | 23.12 | 3.41 | 5.94 | 10.78 | 23.12
| AJY306LALBHH 3 module | 126 + 108 + 72 | 34HP Heat Pump System | [7 empty] | 95.9 | 23.975 | 47.95 | 71.925 | 95.9 | 6.3915
[11 empty] | 25.12 | 3.49 | 6.5 | 12.09 | 25.12
| AJY324LALBHH 3 module | 108 + 108 + 108 | 36HP Heat Pump System | [7 empty] | 100.5 | 25.125 | 50.25 | 75.375 | 100.5 | 6.5455
[11 empty] | 26.88 | 3.69 | 6.51 | 12.33 | 26.88
| AJY342LALBHH 3 module | 126 + 108 + 108 | 38HP Heat Pump System | [7 empty] | 107 | 26.75 | 53.5 | 80.25 | 107 | 6.4706
[11 empty] | 28.88 | 3.77 | 7.07 | 13.64 | 28.88
| AJY360LALBHH 3 module | 126 + 126 + 108 | 40HP Heat Pump System | [7 empty] | 113.5 | 28.375 | 56.75 | 85.125 | 113.5 | 6.4148
[11 empty] | 30.88 | 3.85 | 7.63 | 14.95 | 30.88
| AJY378LALBHH 3 module | 126 + 126 + 126 | 42HP Heat Pump System | [7 empty] | 120 | 30 | 60 | 90 | 120 | 6.3733
[11 empty] | 32.88 | 3.93 | 8.19 | 16.26 | 32.88
| AJY396LALBHH 3 module | 144 + 126 + 126 | 44HP Heat Pump System | [7 empty] | 125 | 31.25 | 62.5 | 93.75 | 125 | 6.3787
[11 empty] | 34.93 | 4.03 | 8.56 | 16.95 | 34.93
| AJY396LALBHH 3 module | 144 + 144 + 126 | 46HP Heat Pump System | [7 empty] | 130 | 32.5 | 65 | 97.5 | 130 | 6.3848
[11 empty] | 36.98 | 4.13 | 8.93 | 17.64 | 36.98
| Total Project (VRF) Cooling Output |  |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  |  | 0 | 0 | 0 | 0 | 0
| Overall Energy Efficiency Ratio |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SEER
| Load Profile - Unknown |  |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!

## SCOP Space Saving Combos
FUJITSU V-III VRF SYSTEMS
SCOP DATA
Enter required quantity to reveal individual or cumulative results.
| Space Saving Combinations | [11 empty] | Input Data
[6 empty] | Heating | [5 empty] | Heating
| Model | Multiple Module Combinations | Description | QTY | Nom Htg kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ |  | Nom HTG kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ | SCOP
[5 empty] | Nom PI | [5 empty] | Nom PI
[6 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe V-III Heat Pump Space Saving Combinations | AJY72LALBH 1 module |  | 8HP Heat Pump System | [7 empty] | 25 | 6.25 | 12.5 | 18.75 | 23.3 | 5.5638
[11 empty] | 5.17 | 0.98 | 1.98 | 3.9 | 5.86
| AJY90LALBH 1 module |  | 10HP Heat Pump System | [7 empty] | 31.5 | 7.875 | 15.75 | 23.625 | 28.7 | 5.3158
[11 empty] | 7.25 | 1.18 | 2.61 | 5.44 | 8.22
| AJY108LALBH 1 module |  | 12HP Heat Pump System | [7 empty] | 37.5 | 9.375 | 18.75 | 28.125 | 32.1 | 5.6006
[11 empty] | 8.65 | 1.3 | 2.95 | 6.27 | 8.86
| AJY126LALBH 1 module |  | 14HP Heat Pump System | [7 empty] | 45 | 11.25 | 22.5 | 33.75 | 38.7 | 5.7354
[11 empty] | 11.17 | 1.48 | 3.57 | 7.01 | 11.45
| AJY144LALBH 1 module |  | 16HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 39.6 | 5.3916
[11 empty] | 13.63 | 1.66 | 4.06 | 9.325 | 12.44
| AJY162LALBH 1 module |  | 18HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 39.6 | 5.1686
[11 empty] | 13.63 | 1.66 | 4.06 | 11.28 | 12.44
| AJY180LALBH 2 module | 90 + 90 | 20HP Heat Pump System | [7 empty] | 63 | 15.75 | 31.5 | 47.25 | 57.4 | 5.3158
[11 empty] | 14.5 | 2.36 | 5.22 | 10.88 | 16.44
| AJY198LALBH 2 module | 126 + 72 | 22HP Heat Pump System | [7 empty] | 70 | 17.5 | 35 | 52.5 | 60 | 5.6489
[11 empty] | 16.34 | 2.46 | 5.55 | 10.91 | 17.31
| AJY216LALBH 2 module | 126 + 90 | 24HP Heat Pump System | [7 empty] | 76.5 | 19.125 | 38.25 | 57.375 | 67.4 | 5.552
[11 empty] | 18.42 | 2.66 | 6.18 | 12.45 | 19.67
| AJY234LALBH 2 module | 144 + 90 | 26HP Heat Pump System | [7 empty] | 81.5 | 20.375 | 40.75 | 61.125 | 68.3 | 5.3557
[11 empty] | 18.42 | 2.84 | 6.67 | 14.765 | 20.66
| AJY252LALH 2 module | 162 + 90 | 28HP Heat Pump System | [7 empty] | 81.5 | 20.375 | 40.75 | 61.125 | 68.3 | 5.2008
[11 empty] | 20.88 | 2.84 | 6.67 | 16.72 | 20.66
| AJY270LALBH 2 module | 144 + 126 | 30HP Heat Pump System | [7 empty] | 95 | 23.75 | 47.5 | 71.25 | 78.3 | 5.543
[11 empty] | 20.88 | 3.14 | 7.63 | 16.335 | 23.89
| AJY288LALBH 2 module | 144 + 144 | 32HP Heat Pump System | [7 empty] | 100 | 25 | 50 | 75 | 79.2 | 5.3916
[11 empty] | 27.26 | 3.32 | 8.12 | 18.65 | 24.88
| AJY306LALBH 2 module | 162 + 144 | 34HP Heat Pump System | [7 empty] | 100 | 25 | 50 | 75 | 79.2 | 5.2695
[11 empty] | 27.26 | 3.32 | 8.12 | 20.605 | 24.88
| AJY324LALBH 2 module | 162 + 162 | 36HP Heat Pump System | [7 empty] | 100 | 25 | 50 | 75 | 79.2 | 5.1686
[11 empty] | 27.26 | 3.32 | 8.12 | 22.56 | 24.88
| AJY342LALBH 3 module | 162 + 90 + 90 | 38HP Heat Pump System | [7 empty] | 113 | 28.25 | 56.5 | 84.75 | 97 | 5.2242
[11 empty] | 28.13 | 4.02 | 9.28 | 22.16 | 28.88
| AJY360LALBH 3 module | 144 + 126 + 90 | 40HP Heat Pump System | [7 empty] | 126.5 | 31.625 | 63.25 | 94.875 | 107 | 5.4819
[11 empty] | 32.05 | 4.32 | 10.24 | 21.775 | 32.11
| AJY378LALBH 3 module | 144 + 144 + 90 | 42HP Heat Pump System | [7 empty] | 131.5 | 32.875 | 65.75 | 98.625 | 107.9 | 5.3683
[11 empty] | 34.51 | 4.5 | 10.73 | 24.09 | 33.1
| AJY396LALBH 3 module | 162 + 144 + 90 | 44HP Heat Pump System | [7 empty] | 131.5 | 32.875 | 65.75 | 98.625 | 107.9 | 5.27
[11 empty] | 34.51 | 4.5 | 10.73 | 26.045 | 33.1
| AJY414LALBH 3 module | 162 + 162 + 90 | 46HP Heat Pump System | [7 empty] | 131.5 | 32.875 | 65.75 | 98.625 | 107.9 | 5.1854
[11 empty] | 34.51 | 4.5 | 10.73 | 28 | 33.1
| AJY432LALBH 3 module | 144 + 144 + 144 | 48HP Heat Pump System | [7 empty] | 150 | 37.5 | 75 | 112.5 | 118.8 | 5.3916
[11 empty] | 40.89 | 4.98 | 12.18 | 27.975 | 37.32
| AJY450LALBH 3 module | 162 + 144 + 144 | 50HP Heat Pump System | [7 empty] | 150 | 37.5 | 75 | 112.5 | 118.8 | 5.3076
[11 empty] | 40.89 | 4.98 | 12.18 | 29.93 | 37.32
| AJY468LALBH 3 module | 162 + 162 + 144 | 52HP Heat Pump System | [7 empty] | 150 | 37.5 | 75 | 112.5 | 118.8 | 5.2338
[11 empty] | 40.89 | 4.98 | 12.18 | 31.885 | 37.32
| AJY486LALBH 3 module | 162 + 162 + 162 | 54HP Heat Pump System | [7 empty] | 150 | 37.5 | 75 | 112.5 | 118.8 | 5.1686
[11 empty] | 40.89 | 4.98 | 12.18 | 33.84 | 37.32
| Total Project (VRF) Cooling Output |  |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  |  | 0 | 0 | 0 | 0 | 0
| Overall COP |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SCOP
| Load Profile - Unknown |  |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!

## SCOP Energy Efficiency Combos
FUJITSU V-III VRF SYSTEMS
SCOP DATA
Enter required quantity to reveal individual or cumulative results.
| Energy Efficiency Combinations | [11 empty] | Input Data
[6 empty] | Heating | [5 empty] | Heating
| Model |  | Description | QTY | Nom Clg kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ |  | Nom HTG kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ | SCOP
[5 empty] | Nom PI | [5 empty] | Nom PI
[6 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
| AJY72LALBH |  | 8HP Heat Pump System | [7 empty] | 25 | 6.25 | 12.5 | 18.75 | 23.3 | 5.5638
[11 empty] | 5.17 | 0.98 | 1.98 | 3.9 | 5.86
| AJY90LALBH |  | 10HP Heat Pump System | [7 empty] | 31.5 | 7.875 | 15.75 | 23.625 | 28.7 | 5.3158
[11 empty] | 7.25 | 1.18 | 2.61 | 5.44 | 8.22
| AJY108LALBH |  | 12HP Heat Pump System | [7 empty] | 37.5 | 9.375 | 18.75 | 28.125 | 32.1 | 5.6006
[11 empty] | 8.65 | 1.3 | 2.95 | 6.27 | 8.86
| AJY126LALBH |  | 14HP Heat Pump System | [7 empty] | 45 | 11.25 | 22.5 | 33.75 | 38.7 | 5.7354
[11 empty] | 11.17 | 1.48 | 3.57 | 7.01 | 11.45
| AJY144LALBH |  | 16HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 39.6 | 5.3916
[11 empty] | 13.63 | 1.66 | 4.06 | 9.325 | 12.44
| AJY162LALBH |  | 18HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 39.6 | 5.1686
[11 empty] | 13.63 | 1.66 | 4.06 | 11.28 | 12.44
2-pipe V-III H.Pump Energy Efficiency Combos | AJY144LALBHH 2 module | 72 + 72 | 16HP Heat Pump System | [7 empty] | 50 | 12.5 | 25 | 37.5 | 46.6 | 5.5638
[11 empty] | 10.34 | 1.96 | 3.96 | 7.8 | 11.72
| AJY162LALBHH 2 module | 90 + 72 | 18HP Heat Pump System | [7 empty] | 56.5 | 14.125 | 28.25 | 42.375 | 52 | 5.4186
[11 empty] | 12.42 | 2.16 | 4.59 | 9.34 | 14.08
| AJY180LALBHH 2 module | 108 + 72 | 20HP Heat Pump System | [7 empty] | 62.5 | 15.625 | 31.25 | 46.875 | 55.4 | 5.5791
[11 empty] | 13.82 | 2.28 | 4.93 | 10.17 | 14.72
| AJY216LALBHH 3 module | 72 + 72 + 72 | 24HP Heat Pump System | [7 empty] | 75 | 18.75 | 37.5 | 56.25 | 69.9 | 5.5638
[11 empty] | 15.51 | 2.94 | 5.94 | 11.7 | 17.58
| AJY234LALBHH 3 module | 90 + 72 + 72 | 26HP Heat Pump System | [7 empty] | 81.5 | 20.375 | 40.75 | 61.125 | 75.3 | 5.4611
[11 empty] | 17.59 | 3.14 | 6.57 | 13.24 | 19.94
| AJY252LALBHH 3 module | 108 + 72 + 72 | 28HP Heat Pump System | [7 empty] | 87.5 | 21.875 | 43.75 | 65.625 | 78.7 | 5.5728
[11 empty] | 18.99 | 3.26 | 6.91 | 14.07 | 20.58
| AJY270LALBHH 3 module | 126 + 72 + 72 | 30HP Heat Pump System | [7 empty] | 95 | 23.75 | 47.5 | 71.25 | 85.3 | 5.633
[11 empty] | 21.51 | 3.44 | 7.53 | 14.81 | 23.17
| AJY288LALBHH 3 module | 108 + 108 + 72 | 32HP Heat Pump System | [7 empty] | 100 | 25 | 50 | 75 | 87.5 | 5.5861
[11 empty] | 22.47 | 3.58 | 7.88 | 16.44 | 23.58
| AJY306LALBHH 3 module | 126 + 108 + 72 | 34HP Heat Pump System | [7 empty] | 107.5 | 26.875 | 53.75 | 80.625 | 94.1 | 5.6392
[11 empty] | 24.99 | 3.76 | 8.5 | 17.18 | 26.17
| AJY324LALBHH 3 module | 108 + 108 + 108 | 36HP Heat Pump System | [7 empty] | 112.5 | 28.125 | 56.25 | 84.375 | 96.4 | 5.6011
[11 empty] | 25.95 | 3.9 | 8.85 | 18.81 | 26.58
| AJY342LALBHH 3 module | 126 + 108 + 108 | 38HP Heat Pump System | [7 empty] | 120 | 30 | 60 | 90 | 102.9 | 5.6479
[11 empty] | 28.47 | 4.08 | 9.47 | 19.55 | 29.17
| AJY360LALBHH 3 module | 126 + 126 + 108 | 40HP Heat Pump System | [7 empty] | 127.5 | 31.875 | 63.75 | 95.625 | 109.5 | 5.6929
[11 empty] | 30.99 | 4.26 | 10.09 | 20.29 | 31.76
| AJY378LALBHH 3 module | 126 + 126 + 126 | 42HP Heat Pump System | [7 empty] | 135 | 33.75 | 67.5 | 101.25 | 116.1 | 5.7353
[11 empty] | 33.51 | 4.44 | 10.71 | 21.03 | 34.36
| AJY396LALBHH 3 module | 144 + 126 + 126 | 44HP Heat Pump System | [7 empty] | 140 | 35 | 70 | 105 | 117 | 5.6016
[11 empty] | 35.97 | 4.62 | 11.2 | 23.345 | 35.35
| AJY396LALBHH 3 module | 144 + 144 + 126 | 46HP Heat Pump System | [7 empty] | 145 | 36.25 | 72.5 | 108.75 | 117.9 | 5.4887
[11 empty] | 38.43 | 4.8 | 11.69 | 25.66 | 36.33
| Total Project (VRF) Cooling Output |  |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  |  | 0 | 0 | 0 | 0 | 0
| Overall Energy Efficiency Ratio |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SCOP
| Load Profile - Unknown |  |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!